Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This Product MasterSpec Section is licensed by ARCOM for limited distribution by Associated Air Balance Council ("Licensee").  The license is subject to revocation by ARCOM subject to the Product MasterSpec License Agreement between ARCOM and Licensee.

A clean version (revisions accepted) and an underline-and-strikeout version of this Section, both of which modify the original MasterSpec text, are distributed by Licensee to assist in specifying Licensee's products.   Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, ARCOM or The American Institute of Architects (AIA).  Neither AIA nor ARCOM are liable in any way for such revisions or for the use of this Product MasterSpec Section by Licensee or any end user to which Licensee distributes this Product MasterSpec Section.  A qualified design professional should review and edit the document to suit project requirements.  For more information, contact Associated Air Balance Council, 1518 K Street, N.W. Washington, DC; phone: (202) 737-0202; fax: (202) 638-4833; Website: www.aabc.com; e-mail: info@aabc.com.  For information about MasterSpec contact ARCOM at (800) 424-5080 or visit www.arcomnet.com.

AABC Recommended Contractor/Subcontractor Provisions to be included in the Form of Agreement between the Contractor and the T&B Subcontractor or stipulated in the Agreement between the Owner and the T&B Agency.

Provide T&B agency one complete set of contract documents, change orders, and approved submittals in digital and hard copy formats

Controls contractor shall provide required BAS hardware, software, personnel and assistance to T&B agency as required to balance the systems. Controls contractor shall also provide trending report to demonstrate that systems are complete.

Coordinate meetings and assistance from suppliers and contractors as required by T&B agency.

Provide additional valves, dampers, sheaves and belts as required by T&B agency.

Flag all manual volume dampers with fluorescent or other high-visibility tape.

Provide access to all dampers, valves, test ports, nameplates and other appurtenances as required by T&B agency.

Replace or repair insulation as required by T&B agency.

Have the HVAC systems at complete operational readiness for T&B to begin. As a minimum verify the following:

Airside:

All ductwork is complete with all terminals installed.

All volume, smoke and fire dampers are open and functional.

Clean filters are installed.

All fans are operating, free of vibration, and rotating in correct direction.

VFD start-up is complete and all safeties are verified.

System readiness checklists are completed and returned to T&B agency.

Hydronics:

Piping is complete with all terminals installed.

Water treatment is complete.

Systems are flushed, filled and air purged.

Strainers are pulled and cleaned.

Control valves are functioning per the sequence of operation.

All shutoff and balance valves have been verified to be 100% open.

Pumps are started, and proper rotation is verified.

Pump gauge connections are installed directly at the pump inlet and outlet flange or in discharge and suction pipe prior to any valves or strainers.

VFD start-up is complete and all safeties have been verified.

System readiness checklists are completed and returned to T&B agency.

Promptly correct deficiencies identified during T&B.

Maintain a construction schedule that allows the T&B agency to complete work prior to occupancy.

SECTION 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

Retain only subparagraphs below that identify the systems that are included in the Project.

          - Balancing Air Systems:

            - Constant-volume air systems.

            - Dual-duct systems.

            - Variable-air-volume systems.

            - Multizone systems.

            - Induction-unit systems.

          - Balancing Hydronic Piping Systems:

            - Constant-flow hydronic systems.

            - Variable-flow hydronic systems.

            - Primary-secondary hydronic systems.

Tests described in the “Additional Tests” section are considered beyond the standard test and balance scope, and should only be included if the design professional believes the additional time and expense are warranted.

          - Additional Tests

            - Seasonal tests.

            - Sound testing.

            - Vibration testing.

            - Duct leakage testing.

            - Controls verification.

      - DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

        - AABC:  Associated Air Balance Council.

        - T&B: Testing, adjusting, and balancing

        - T&B Agency:  An independent entity certified by AABC to perform testing and balancing work.

        - TBE:  AABC certified test and balance engineer.

        - TBT:	 AABC certified test and balance technician.

        - HVAC:  Heating, ventilating, and air conditioning.

        - BAS:  Building automation systems.

        - Contract documents: the mechanical drawings and test and balance specification

        - NC: noise criteria

        - RC: room criteria

          - T&B

          - INFORMATIONAL SUBMITTALS

Coordinate timing of submittals with Section 013200 "Construction Progress Documentation" and Section 013300 "Submittal Procedures."

See Editing Instruction No. 1 in the Evaluations for timing requirements of submittals.

        - Qualification Data:  Within [30] [45] [60] [90] <Insert number> days of Contractor's Notice to Proceed, submit documentation T&B of AABC certification of T&B agency and personnel, including a sample copy of the AABC "National Performance Guaranty." If not submitted within the timeframe specified, the engineer has the right to choose an AABC agency at the Contractor’s expense.

        - Strategies and Procedures Plan:  Within [30] [60] [90] <Insert number> days of Contractor's Notice to Proceed, submit T&B strategies and step-by-step procedures as specified in "Preparation" Article.

        - System Readiness Checklists:  Within [30] [60] [90] <Insert number> days of Contractor's Notice to Proceed, submit system readiness checklists as specified in "Preparation" Article to be used and filled out by systems Installers verifying that systems are ready for T&B.

        - Examination Report:  Within [30] [60] [90] <Insert number> days of Contractor's Notice to Proceed, provide a summary report of the examination review required in Part 3 “Examination”, if issues are discovered that may preclude the proper testing and balancing of the systems.

        - Certified T&B reports:  Within [14] [21] [30] <Insert number> days of completion of balancing work, submit AABC-certified T&B report.

          - Submit one copy of the final T&B Report directly to the design professional of record.  Provide five additional copies to the contractor.

      - QUALITY ASSURANCE

        - T&B Agency Qualifications:  Engage a T&B entity certified by AABC.

          - T&B Field Supervisor:  Employee of the T&B Agency who is certified by AABC.

          - T&B Technician:  Employee of the T&B Agency and who is certified by AABC as a TBT.

If retaining first option in first paragraph below, verify that the T&B conference is in scope of design services.

        - T&B Conference: If requested by the [Architect] [Owner] [Construction Manager] [Commissioning Authority] after approval of the T&B Agency’s submittals, meet to develop a mutual understanding of the details. The T&B agency shall be provided a minimum of [14] <Insert number> days' advance notice of scheduled meeting time and location.

          - Agenda Items:

Coordinate requirements in subparagraphs below with Section 013100 "Project Management and Coordination."

            - The examination report.

            - The Strategies and Procedures plan.

            - Systems readiness checklists.

            - Coordination and cooperation of trades and subcontractors.

            - Coordination of documentation and communication flow.

        - TBT shall perform the following:

          - Review field data reports to validate accuracy of data and to prepare certified T&B reports.

          - Certify that the T&B team complied with the approved T&B plan and the procedures specified and referenced in this Specification.

          - Certify the T&B report.

        - T&B Report Forms:  Use approved forms submitted with the Strategies and Procedures Plan.

        - Instrumentation Type, Quantity, Accuracy, and Calibration:  As described in the "AABC National Standards for Total System Balance."

      - PROJECT CONDITIONS

Retain one of two paragraphs below.  Delete article if there will be no occupancy during T&B Work.

        - Full Owner Occupancy:  Owner will occupy the site and existing building during entire T&B period.  Cooperate with Owner during T&B operations to minimize conflicts with Owner's operations.

Retain paragraph below if Owner might occupy completed areas of building.

        - Partial Owner Occupancy:  Owner may occupy completed areas of building before Substantial Completion.  Cooperate with Owner during T&B operations to minimize conflicts with Owner's operations.

        - PRODUCTS (Not Applicable)

- EXECUTION

      - T&B AGENCY

Retain this article and list of T&B Agencies to limit Contractor's choice of T&B contractors; delete to allow Contractor to select any contractor meeting qualification requirements.

        - Subject to compliance with requirements, engage one of the following the following AABC certified T&B Agencies:

          - <Insert the T&B Agency's name>.

      - EXAMINATION

See Editing Instruction No. 2 in the Evaluations for discussion of the Contract Documents review.

        - Examine the Contract Documents to become familiar with Project requirements and to discover conditions in systems' designs that may preclude proper T&B of systems and equipment.

        - Examine systems for installed balancing devices, such as test ports, gage cocks, thermometer wells, flow-control devices, balancing valves and fittings, and manual volume dampers.  Note the locations of devices that are not accessible for testing and balancing.

        - Examine the approved submittals for HVAC systems and equipment.

        - Examine ceiling plenums and underfloor air plenums used for supply, return, or relief air to verify that are properly separated from adjacent areas.  Verify that penetrations in plenum walls are sealed and fire-stopped if required.

        - Examine equipment performance data including fan and pump curves.

        - Examine HVAC equipment and verify that bearings are greased, belts are aligned and tight, clean permanent filters are installed, and equipment with functioning controls is ready for operation.

        - Examine terminal units, such as variable-air-volume boxes, and verify that they are accessible and their controls are connected, configured by the controls contractor, and functioning.

        - Examine strainers to verify that mechanical contractor has replaced startup screens with permanent screens and that all strainers have been cleaned.

        - Examine two-way valves for proper installation and function.

        - Examine three-way valves for proper installation for their intended function of diverting or mixing fluid flows.

        - Examine heat-transfer coils for correct piping connections and for clean and straight fins.

        - Examine air vents to verify that mechanical contractor has removed all air from all hydronic systems.

        - PREPARATION

        - Prepare a T&B plan that includes the following:

          - Equipment and systems to be tested.

          - Strategies and step-by-step procedures for balancing the systems.

          - Instrumentation to be used.

          - Sample forms with specific identification for all equipment.

        - Prepare system-readiness checklists, as described in the "AABC National Standards for Total System Balance," for use by systems installers in verifying system readiness for T&B. These shall include, at a minimum, the following:

          - Airside:

            - Ductwork is complete with terminals installed.

            - Volume, smoke and fire dampers are open and functional.

            - Clean filters are installed.

            - Fans are operating, free of vibration, and rotating in correct direction.

            - Variable-frequency controllers' start-up is complete and safeties are verified.

            - Automatic temperature-control systems are operational.

            - Ceilings are installed.

            - Windows and doors are installed.

            - Suitable access to balancing devices and equipment is provided.

          - Hydronics:

            - Piping is complete with terminals installed.

            - Water treatment is complete.

            - Systems are flushed, filled and air purged.

            - Strainers are pulled and cleaned.

            - Control valves are functioning per the sequence of operation.

            - Shutoff and balance valves have been verified to be 100 percent open.

            - Pumps are started and proper rotation is verified.

            - Pump gage connections are installed directly at pump inlet and outlet flanges or in discharge and suction pipe prior to valves or strainers.

            - Variable-frequency controllers' start-up is complete and safeties are verified.

            - Suitable access to balancing devices and equipment is provided.

      - GENERAL PROCEDURES FOR TESTING AND BALANCING

        - Perform testing and balancing procedures on each system according to the procedures contained in AABC's "National Standards for Total System Balance" and in this Section.

LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1, Section 7.2.2 - "Air Balancing."  ASHRAE 62.1 requires that ventilation systems be balanced according to ASHRAE 111 or SMACNA's "HVAC Systems - Testing, Adjusting, and Balancing," or be equivalent at least to extent necessary to verify compliance with the standard.  The AABC National Standards meet or exceed this requirement.

        - Cut insulation, ducts, pipes, and equipment cabinets for installation of test probes to the minimum extent necessary for T&B procedures.

        - Mark equipment and balancing devices, including damper-control positions, valve position indicators, fan-speed-control levers, and similar controls and devices, with paint or other suitable, permanent identification material to show final settings.

        - Take and report testing and balancing measurements in inch-pound (IP)units.

      - GENERAL PROCEDURES FOR BALANCING AIR SYSTEMS

        - Prepare test reports for both fans and outlets.  Obtain approved submittals and recommended testing procedures.  Crosscheck the summation of required outlet volumes with required fan volumes.

        - Prepare single-line schematic diagram of systems for the purpose of identifying HVAC components.

        - For variable-air-volume systems, develop a plan to simulate diversity.

        - Determine the best locations in main and branch ducts for accurate duct-airflow measurements.

        - Locate start-stop and disconnect switches, electrical interlocks, and motor starters.

        - Verify that motor starters are equipped with properly sized thermal protection.

        - Check condensate drains for proper connections and functioning.

        - Check for proper sealing of air-handling-unit components.

      - PROCEDURES FOR CONSTANT-VOLUME AIR SYSTEMS

Retain this article if using constant-volume air systems.

        - Adjust fans to deliver total indicated airflows within the maximum allowable fan speed listed by fan manufacturer.

          - Measure total airflow.

            - Set outside air, return air and relief air dampers for proper position that simulates minimum outdoor air conditions.

            - Where duct conditions allow, measure airflow by Pitot-tube traverse. If necessary, perform multiple Pitot-tube traverses to obtain total airflow.

            - Where duct conditions are not suitable for Pitot-tube traverse measurements, a coil traverse may be acceptable.

            - If a reliable Pitot-tube traverse or coil traverse is not possible, measure airflow at terminals and calculate the total airflow.

          - Measure fan static pressures as follows:

            - Measure static pressure directly at the fan outlet or through the flexible connection.

            - Measure static pressure directly at the fan inlet or through the flexible connection.

            - Measure static pressure across each component that makes up the air-handling system.

            - Report any artificial loading of filters at the time static pressures are measured.

          - Do not make fan-speed adjustments that result in motor overload.  Consult equipment manufacturers about fan-speed safety factors.  Modulate dampers and measure fan-motor amperage to ensure that no overload will occur.  Measure amperage in full-cooling, full-heating, economizer, and any other operating mode to determine the maximum required brake horsepower.

        - Adjust volume dampers for main duct, submain ducts, and major branch ducts to indicated airflows.

          - Measure airflow of submain and branch ducts.

          - Adjust sub-main and branch duct volume dampers for specified airflow.
Re-measure each sub-main and branch duct after all have been adjusted.

        - Adjust air inlets and outlets for each space to indicated airflows.

          - Set airflow patterns of adjustable outlets for proper distribution without drafts.

          - Measure airflow at all inlets and outlets.

          - Adjust each inlet and outlet for specified airflow.

          - Re-measure each inlet and outlet after all have been adjusted.

        - Verify final system conditions.

          - Re-measure and confirm minimum outdoor air, return and relief airflows are within design. Readjust to design if necessary.

          - Re-measure and confirm total airflow is within design.

          - Re-measure all final fan operating data, rpms, volts, amps, static profile.

          - Mark all final settings.

          - Test system in economizer mode. Verify proper operation and adjust, if necessary.

          - Measure and record all operating data.

          - Record final fan-performance data.

      - PROCEDURES FOR DUAL-DUCT SYSTEMS

Retain this article if using dual-duct systems.

        - Adjust the dual-duct systems as follows:

          - Verify that the system static pressure sensor is located 2/3 of the distance down the duct from the fan discharge. On systems with separate hot deck and cold deck fans, verify the location of the sensor on each deck.

          - Verify that the system is under static pressure control.

          - Select the terminal unit that is most critical to the supply-fan airflow. Measure inlet static pressure, and adjust system static pressure control setpoint so the entering static pressure for the critical terminal unit is not less than the sum of the terminal-unit manufacturer's recommended minimum inlet static pressure plus the static pressure needed to overcome terminal-unit discharge system losses.

          - Calibrate and balance each terminal unit’s hot deck and cold deck for maximum and minimum design airflow as follows:

            - Adjust controls so that terminal is calling for full cooling. (Note: some controllers require starting with minimum setpoint. Verify calibration procedure for specific project.)

            - Measure airflow and adjust calibration factors as required for design cold deck maximum airflow and hot deck minimum airflow. Record calibration factors.

            - When maximum airflow is correct, balance the air outlets downstream from terminal units.

            - Adjust controls so that terminal is calling for full heating.

            - Measure airflow and adjust calibration factors as required for design cold deck minimum airflow and hot deck maximum airflow. Record calibration factors. If no minimum calibration is available, note any deviation from design airflow.

          - After all terminals have been calibrated and balanced, test and adjust system for total airflow. Adjust fans to deliver total design airflows within the maximum allowable fan speed listed by fan manufacturer.

            - Set outside air, return air and relief air dampers for proper position that simulates minimum outdoor air conditions.

            - Set terminals for maximum airflow. If system design includes diversity (cooling coil or fan), adjust terminals for maximum and minimum airflow so that connected total matches cooling coil or fan selection and simulates actual load in the building. In systems with separate hot deck and cold deck fans, diversity consideration applies to each individual fan.

            - Where duct conditions allow, measure airflow by Pitot-tube traverse. If necessary, perform multiple Pitot-tube traverses to obtain total airflow.

            - Where duct conditions are not suitable for Pitot-tube traverse measurements, a coil traverse may be acceptable.

            - If a reliable Pitot-tube traverse or coil traverse is not possible, measure airflow at terminals and calculate the total airflow.

          - Measure the fan(s) static pressures as follows:

            - Measure static pressure directly at the fan outlet or through the flexible connection.

            - Measure static pressure directly at the fan inlet or through the flexible connection.

            - Measure static pressure across each component that makes up the air-handling system.

            - Report any artificial loading of filters at the time static pressures are measured.

          - Set final return and outside airflow to the fan(s) while operating at maximum return airflow and minimum outdoor airflow.

            - Balance the return-air ducts and inlets the same as described for constant-volume air systems.

            - Verify all terminal units are meeting design airflow under system maximum flow.

          - Re-measure the inlet static pressure at the most critical terminal unit and adjust the system static pressure setpoint to the most energy-efficient setpoint to maintain the optimum system static pressure. Record setpoint and give to controls contractor.

          - Verify final system conditions as follows:

            - Re-measure and confirm minimum outdoor air, return and relief airflows are within design. Readjust to design if necessary.

            - Re-measure and confirm total airflow is within design.

            - Re-measure all final fan operating data, rpms, volts, amps, static profile.

            - Mark all final settings.

            - Test system in economizer mode. Verify proper operation and adjust, if necessary. Measure and record all operating data.

            - Verify tracking between supply and return fans.

          - Record final fan-performance data.

      - PROCEDURES FOR VARIABLE-AIR-VOLUME SYSTEMS

Retain this article if using variable-air-volume systems.

        - Adjust the variable-air-volume systems as follows:

          - Verify that the system static pressure sensor is located 2/3 of the distance down the duct from the fan discharge.

          - Verify that the system is under static pressure control.

          - Select the terminal unit that is most critical to the supply-fan airflow. Measure inlet static pressure, and adjust system static pressure control setpoint so the entering static pressure for the critical terminal unit is not less than the sum of the terminal-unit manufacturer's recommended minimum inlet static pressure plus the static pressure needed to overcome terminal-unit discharge system losses.

          - Calibrate and balance each terminal unit for maximum and minimum design airflow as follows

            - Adjust controls so that terminal is calling for maximum airflow (note some controllers require starting with minimum airflow. Verify calibration procedure for specific project).

            - Measure airflow and adjust calibration factor as required for design maximum airflow. Record calibration factor.

            - When maximum airflow is correct, balance the air outlets downstream from terminal units.

            - Adjust controls so that terminal is calling for minimum airflow.

            - Measure airflow and adjust calibration factor as required for design minimum airflow. Record calibration factor. If no minimum calibration is available, note any deviation from design airflow.

            - When in full cooling or full heating, ensure that there is no mixing of hot deck and cold deck airstreams unless so designed.

            - On constant volume terminals, in critical areas where room pressure is to be maintained, verify that the airflow remains constant over the full range of full cooling to full heating. Note any deviation from design airflow or room pressure.

          - After all terminals have been calibrated and balanced, test and adjust system for total airflow. Adjust fans to deliver total design airflows within the maximum allowable fan speed listed by fan manufacturer.

            - Set outside air, return air and relief air dampers for proper position that simulates minimum outdoor air conditions.

            - Set terminals for maximum airflow. If system design includes diversity, adjust terminals for maximum and minimum airflow so that connected total matches fan selection and simulates actual load in the building.

            - Where duct conditions allow, measure airflow by Pitot-tube traverse. If necessary, perform multiple Pitot-tube traverses to obtain total airflow.

            - Where duct conditions are not suitable for Pitot-tube traverse measurements, a coil traverse may be acceptable.

            - If a reliable Pitot-tube traverse or coil traverse is not possible, measure airflow at terminals and calculate the total airflow.

          - Measure fan static pressures as follows:

            - Measure static pressure directly at the fan outlet or through the flexible connection.

            - Measure static pressure directly at the fan inlet or through the flexible connection.

            - Measure static pressure across each component that makes up the air-handling system.

            - Report any artificial loading of filters at the time static pressures are measured.

          - Set final return and outside airflow to the fan while operating at maximum return airflow and minimum outdoor airflow.

            - Balance the return-air ducts and inlets the same as described for constant-volume air systems.

            - Verify all terminal units are meeting design airflow under system maximum flow.

          - Re-measure the inlet static pressure at the most critical terminal unit and adjust the system static pressure setpoint to the most energy-efficient setpoint to maintain the optimum system static pressure. Record setpoint and give to controls contractor.

          - Verify final system conditions as follows:

            - Re-measure and confirm minimum outdoor air, return and relief airflows are within design. Readjust to design if necessary.

            - Re-measure and confirm total airflow is within design.

            - Re-measure all final fan operating data, rpms, volts, amps, static profile.

            - Mark all final settings.

            - Test system in economizer mode. Verify proper operation and adjust, if necessary. Measure and record all operating data.

            - Verify tracking between supply and return fans.

      - PROCEDURES FOR MULTIZONE SYSTEMS

Retain this article if using multi-zone systems.

        - Position the unit’s automatic zone dampers for maximum flow through the cooling coil.

        - The procedures for multi-zone systems will follow the procedures for constant volume systems, utilizing the zone balancing dampers to achieve the indicated airflow within the zone.

        - After balancing, place the unit’s automatic zone dampers for maximum heating flow. Retest zone airflows and record any variances.

      - PROCEDURES FOR INDUCTION-UNIT SYSTEMS

Retain this article if using induction units.

        - The basic procedures for induction-unit systems will follow the procedures for constant volume systems.

        - Balance airflow to each induction unit by measuring the nozzle pressure and comparing it to the manufacturer’s published data for nozzle pressure versus CFM. Adjust the unit’s inlet damper to achieve the required nozzle pressure for design CFM.

      - GENERAL PROCEDURES FOR HYDRONIC SYSTEMS

        - Prepare test reports for pumps, coils and heat exchangers. Obtain approved submittals and any manufacturer-recommended testing procedures. Crosscheck the summation of required coil and heat exchanger flow rates with pump design flow rate.

        - Verify that hydronic systems are ready for testing and balancing:

          - Check liquid level in expansion tank.

          - Check that makeup water-has adequate pressure to highest vent.

          - Check that control valves are in their proper position.

          - Locate start-stop and disconnect switches, electrical interlocks, and motor starters.

          - Verify that motor starters are equipped with properly sized thermal protection.

          - Check that air has been purged from the system.

      - PROCEDURES FOR CONSTANT-FLOW HYDRONIC SYSTEMS

Retain this article if using constant-flow hydronic systems.

        - Adjust pumps to deliver total design gpm.

          - Measure total water flow.

            - Position valves for full flow through coils.

            - Measure flow by main flow meter, if installed.

            - If main flow meter is not installed determine flow by pump total dynamic head (TDH) or exchanger pressure drop.

          - Measure pump TDH as follows:

            - Measure discharge pressure directly at the pump outlet flange or in discharge pipe prior to any valves.

            - Measure inlet pressure directly at the pump inlet flange or in suction pipe prior to any valves or strainers.

            - Convert pressure to head and correct for differences in gauge heights.

            - Verify pump impeller size by measuring the TDH with the discharge valve closed. Note the point on manufacturer's pump curve at zero flow and verify that the pump has the intended impeller size.

            - With all valves open, read pump TDH. Adjust pump discharge valve until design water flow is achieved.

          - Monitor motor performance during procedures and do not operate motor in an overloaded condition.

        - Adjust flow measuring devices installed in mains and branches to design water flows.

          - Measure flow in main and branch pipes.

          - Adjust main and branch balance valves for design flow.

          - Re-measure each main and branch after all have been adjusted.

        - Adjust flow measuring devices installed at terminals for each space to design water flows.

          - Measure flow at all terminals.

          - Adjust each terminal to design flow.

          - Re-measure each terminal after all have been adjusted.

          - Position control valves to bypass the coil and adjust the bypass valve to maintain design flow.

          - Perform temperature tests after all flows have been balanced.

        - For systems with pressure-independent valves at the terminals:

          - Measure differential pressure and verify that it is within manufacturer’s specified range.

          - Perform temperature tests after all flows have been verified.

        - For systems without pressure-independent valves or flow measuring devices at the terminals:

          - Measure and balance coils by either coil pressure drop or temperature method.

          - If balanced by coil pressure drop, perform temperature tests after all flows have been verified.

        - Verify final system conditions as follows:

          - Re-measure and confirm that total water flow is within design.

          - Re-measure all final pumps' operating data, TDH, volts, amps, static profile.

          - Mark all final settings.

        - Verify that all memory stops have been set.

      - PROCEDURES FOR VARIABLE-FLOW HYDRONIC SYSTEMS

Retain this article if using variable-flow hydronic systems.

        - Balance systems with automatic two- and three-way control valves by setting systems at maximum flow through heat-exchange terminals and proceed as specified above for hydronic systems.

        - Adjust the variable-flow hydronic system as follows:

          - Verify that the differential-pressure sensor is located per the contract documents.

          - Determine if there is diversity in the system.

        - For systems with no diversity:

          - Follow procedures outlined in "Procedures for Constant-Flow Hydronic Systems" Article.

          - Prior to verifying final system conditions, determine the system differential-pressure set point.

          - If the pump discharge valve was used to set total system flow with variable-frequency controller at 60 Hz, at completion open discharge valve 100 percent and allow variable-frequency controller to control system differential-pressure set point. Record pump data under both conditions.

          - Mark all final settings and verify that all memory stops have been set.

        - For systems with diversity:

          - Determine diversity factor.

          - Simulate system diversity by closing required number of control valves, as approved by the design engineer.

          - Follow procedures outlined in "Procedures for Constant-Flow Hydronic Systems" Article.

          - Open control valves that were shut. Close a sufficient number of control valves that were previously open to maintain diversity, and balance the terminals that were just opened.

          - Prior to verifying final system conditions, determine the system differential-pressure set point.

          - If the pump discharge valve was used to set total system flow with variable-frequency controller at 60 Hz, at completion open discharge valve 100 percent and allow variable-frequency controller to control system differential-pressure set point. Record pump data under both conditions.

          - Mark all final settings and verify that all memory stops have been set.

      - PROCEDURES FOR PRIMARY-SECONDARY HYDRONIC SYSTEMS

Retain this article if using primary-secondary hydronic systems.

        - Follow general procedures for hydronic systems.

        - Balance the primary circuit flow first.

        - Balance the secondary circuits after the primary circuits are complete.

      - PROCEDURES FOR STEAM SYSTEMS

Retain this article if using steam systems.

        - Check settings and operation of automatic temperature-control valves, self-contained control valves, and pressure-reducing valves.  Record final settings.

        - Check settings and operation of each safety valve.  Record settings.

        - Verify the operation of each steam trap.

      - PROCEDURES FOR HEAT EXCHANGERS

Retain this article if using heat exchangers.

        - Balance water flow to within specified tolerances.

        - Measure inlet and outlet water temperatures.

        - Check settings and operation of safety and relief valves.  Record settings.

      - PROCEDURES FOR MOTORS

Retain this article if using motors.

        - Motors, 1/2 HP and Larger:  Test at final balanced conditions and record the following data:

          - Manufacturer's name, model number, and serial number.

          - Motor horsepower rating.

          - Motor rpm.

          - Phse/Hertz (Hz)

          - Nameplate and measured voltage, each phase.

          - Nameplate and measured amperage, each phase.

          - Starter size and thermal-protection-element rating.

          - Service factor and frame size.

        - Motors Driven by Variable-Frequency Controllers:  Test the manual bypass of the controller to prove proper operation.

      - PROCEDURES FOR CHILLERS

Retain this article if using chillers.

        - Balance water flow through each evaporator[ and condenser] to within specified tolerances with all pumps operating per design sequence.  Record the following data with each chiller operating at design conditions:

          - Evaporator-water entering and leaving temperatures, pressure drop, and water flow.

          - For water-cooled chillers, condenser-water entering and leaving temperatures, pressure drop, and water flow.

          - Power factor if shown on the chiller display panel.

          - Kilowatt input if shown on the chiller display panel.

          - Capacity:  Calculate in tons of cooling.

          - For air-cooled chillers, verify condenser-fan rotation and record fan and motor data including number of fans and entering- and leaving-air temperatures.

      - PROCEDURES FOR COOLING TOWERS

Retain this article if using cooling towers.

Tests in paragraph below do not comply with CTI STD-105, "Acceptance Test Code."

        - Balance total condenser-water flows to the towers. Measure and record the following data:

          - Condenser-water flow to each cell of the cooling tower.

          - Entering- and leaving-water temperatures.

          - Wet- and dry-bulb temperatures of entering air.

          - Wet- and dry-bulb temperatures of leaving air.

          - Condenser-water flow through bypass.

          - Fan and motor operating data.

      - PROCEDURES FOR CONDENSING UNITS

Retain this article if using condensing units.

        - Verify proper rotation of fans.

        - Measure entering- and leaving-air temperatures.

        - Record fan and motor operating data.

      - PROCEDURES FOR BOILERS

Retain this article if using boilers.

        - Hydronic Boilers:

          - Measure and record entering- and leaving-water temperatures.

          - Measure and record water flow.

          - Record relief valve pressure setting.

        - Steam Boilers:

          - Measure and record entering-water temperature

          - Measure and record feed water flow.

          - Measure and record leaving-steam pressure and temperature

          - Record relief valve pressure setting.

      - PROCEDURES FOR HEAT-TRANSFER COILS

Retain this article if using hear-transfer coils.

        - Measure, adjust, and record the following data for each water coil:

          - Entering- and leaving-water temperature.

          - Water flow rate.

          - Water pressure drop for major (more than 20 gpm) equipment coils, excluding unitary equipment such as reheat coils, unit heaters, fan-coil units, etc.

          - Dry-bulb temperature of entering and leaving air.

          - Wet-bulb temperature of entering and leaving air for cooling coils.

          - Airflow.

        - Measure, adjust, and record the following data for each electric heating coil:

          - Nameplate data.

          - Airflow.

          - Entering- and leaving-air temperature at full load.

          - Voltage and amperage input of each phase at full load.

          - Calculated kilowatt at full load.

          - Fuse or circuit-breaker rating for overload protection.

        - Measure, adjust, and record the following data for each steam coil:

          - Dry-bulb temperature of entering and leaving air.

          - Airflow.

          - Inlet steam pressure.

        - Measure, adjust, and record the following data for each refrigerant coil:

          - Dry-bulb temperature of entering and leaving air.

          - Wet-bulb temperature of entering and leaving air.

          - Airflow.

      - PROCEDURES FOR TESTING, ADJUSTING, AND BALANCING EXISTING SYSTEMS

Retain this article if Project includes existing systems.

        - Perform a preconstruction inspection of existing equipment that is to remain and be reused.

          - Measure and record the operating speed, airflow, and static pressure of each fan.

          - Measure motor voltage and amperage.  Compare the values to motor nameplate information.

          - Check the condition of filters.

          - Check the condition of coils.

          - Report on the operating condition of the equipment and the results of the measurements taken.  Report deficiencies.

        - Before performing testing and balancing of existing systems, inspect existing equipment that is to remain and be reused to verify that existing equipment has been cleaned and refurbished.  Verify the following:

          - New filters are installed.

          - Coils are clean and fins combed.

          - Drain pans are clean.

          - Fans are clean.

          - Deficiencies noted in the preconstruction report are corrected.

        - Perform testing and balancing of existing systems to the extent that existing systems are affected by the renovation work.

          - Compare the indicated airflow of the renovated work to the measured fan airflows, and determine the new fan speed.

          - Verify that the indicated airflows of the renovated work result in fan speeds that are within the acceptable limits defined by equipment manufacturer.

          - Adjust fan speeds within the limits of the installed sheaves and belts to achieve design airflow.

          - Balance system to design airflows indicated.

      - TOLERANCES

        - Set HVAC system's air flow rates and water flow rates within the following tolerances:

          - Supply, Return, and Exhaust Fans and Equipment with Fans:  Plus or minus 10 percent.

          - Air Outlets and Inlets:  Plus or minus 10 percent.

          - Heating-Water Flow Rate:  Plus or minus 10 percent.

          - Cooling-Water Flow Rate:  Plus or minus 10 percent.

        - Maintaining pressure relationships as designed shall have priority over the tolerances specified above.

      - FINAL TEST AND BALANCE REPORT

        - The report shall be a complete record of the HVAC system performance, including conditions of operation, items outstanding, and any deviations found during the T&B process. The final report also provides a reference of actual operating conditions for the owner and/or operations personnel. All measurements and test results that appear in the reports must be made on site and dated by the AABC technicians or test and balance engineers.

        - The report must be organized by systems and shall include the following information as a minimum:

          - Title Page:

            - AABC certified company name

            - Company address

            - Company telephone number

            - Project identification number

            - Location

            - Project Architect

            - Project Engineer

            - Project Contractor

            - Project number

            - Date of report

            - AABC Certification Statement

            - Name, signature, and certification number of AABC TBE

          - Table of Contents.

          - AABC National Performance Guaranty.

          - Report Summary:

            - The summary shall include a list of items that do not meet design tolerances, with information that may be considered in resolving deficiencies.

          - Instrument List:

            - Type.

            - Manufacturer.

            - Model.

            - Serial Number.

            - Calibration Date.

          - T&B Data:

            - Provide test data for specific systems and equipment as required by the most recent edition of the "AABC National Standards."

        - One copy of the final test and balance report shall be sent directly to the [design professional] [Architect] of record. Provide five additional copies to the contractor.

          - VERIFICATION OF T&B REPORT

        - Final Verification:

          - After testing and balancing is complete and accurately documented in the final report, request that a final verification be made by [design professional] [Architect] [Commissioning Authority].

          - The T&B Agency shall conduct the verification in the presence of [design professional] [Architect] [Commissioning Authority].

          - [Design Professional] [Architect] [Commissioning Authority] shall randomly select measurements, documented in the final report, to be rechecked.  Rechecking shall be limited to either 10 percent of the total measurements recorded or the extent of measurements that can be accomplished in a normal 8-hour business day.

          - If rechecks yield measurements that differ from the measurements documented in the final report by more than the tolerances allowed, the measurements shall be noted as "FAILED."

          - If the number of "FAILED" measurements is greater than 10 percent of the total measurements checked during the final verification, the testing and balancing shall be considered incomplete.

        - REVERIFICATION

If the T&B Work is considered incomplete, proceed as follows:

        - T&B Agency shall recheck all measurements and make adjustments as required to complete the balancing.  Revise the final report and balancing device settings to include all changes; resubmit the final report and request a second verification.

        - If the second verification also fails, [Owner][Design professional] [Architect] may contact AABC Headquarters regarding the AABC National Performance Guaranty.

      - ADDITIONAL TESTS

        - Seasonal Periods:  If initial T&B procedures were not performed during near-peak conditions, the engineer may request a temperature recheck to further verify performance at near-peak conditions.

        - Sound Testing

          - After the systems are balanced  and the spaces are architecturally complete, read and record sound levels at [5] [10] [15] <Insert number> locations as designated by the [design professional] [Architect] of record.

          - Instrumentation:

            - The sound-testing meter shall be a portable, general-purpose testing meter consisting of a microphone, processing unit, and readout.

            - The sound-testing meter shall be capable of showing fluctuations at minimum and maximum levels, and measuring the equivalent continuous sound pressure level (LEQ).

            - The sound-testing meter must be capable of using 1/3 octave band filters to measure mid-frequencies from 31.5 HZ to 8000 HZ.

            - The accuracy of the sound-testing meter shall be ±1 decibel.

          - Test Procedures

            - Perform test at the quietest background noise period. Note any cause of unpreventable sound that may affect the test outcome.

            - Equipment should be operating at design values.

            - Calibrate the sound-testing meter prior to taking measurements.

            - Use a microphone suitable for the type of noise levels measured that is compatible with the meter. Provide a windshield for outside or in-duct measurements.

            - Record a set of background measurements in dB(A), and sound pressure levels in the eight un-weighted octave bands [63 HZ to 8000 HZ (NC)] [31.5 HZ to 4000 HZ (RC)] with the equipment off.

            - Take sound readings in dB(A), and sound pressure levels in the eight un-weighted octave bands [63 HZ to 8000 HZ (NC)] [31.5 HZ to 4000 HZ (RC)] with the equipment on.

            - Take readings no closer than 3’ from a wall or from the operating equipment, and approximately 5’ from the floor, with the meter held or mounted on a tripod.

            - For outdoor measurements, move the sound-testing meter slowly and scan the area that has the greatest exposure to the noise source being tested. (This type of reading is generally performed using the A-Weighted scale).

          - Reporting

            - The report must record: the location, the system tested, the dB(A) reading, and the sound pressure level in each octave band with equipment on and off.

            - Plot all the sound pressure levels on the [NC] [RC] work sheet, with the equipment on and off.

        - Vibration Testing:

          - After the systems are balanced and the spaces are architecturally complete, read and record vibration levels on all equipment with motor horsepower equal to or greater than [10] [15] [25]<Insert number> hp.

          - Instrumentation:

            - The vibration meter should be portable, battery-operated, and microprocessor-controlled, with or without a built-in printer.

            - The meter shall automatically identify engineering units, filter bandwidth, amplitude and frequency scale values.

            - The meter shall be able to measure machine vibration displacement in mils of deflection, velocity in inches per second, and acceleration in inches per second squared.

          - Test Procedures:

            - Verify that the vibration meter calibration date is current before taking readings.

            - To ensure accurate readings, verify that the accelerometer has a clean, flat surface and is mounted properly.

            - With the unit running, set up the vibration meter in a safe, secure location. Connect the transducer to the meter with the proper cables. Hold the magnetic tip of the transducer on top of the bearing, and measure the unit in mils of deflection. Record the measurement, then move the transducer to the side of the bearing, and record in mils of deflection. Record an axial reading in mils of deflection by holding the nonmagnetic, pointed transducer tip on the end of the shaft.

            - Change the vibration meter to velocity (inches per second) measurements. Repeat and record the above measurements.

            - Record the CPM or the RPM.

            - Read each bearing on the motor, fan, and/or pump as required. Track and record vibration levels from the rotating component through the casing to the base.

          - Reporting

            - The report must record the location and the system tested.

            - Include horizontal-vertical-axial measurements for all tests.

            - Verify that vibration limits follow specifications, or, if not specified, follow the “General Machinery Vibration Severity Chart” or “Vibration Acceleration General Severity Chart” from the AABC National Standards. Acceptable levels of vibration are normally “Smooth” to “Good.”

            - Include in the report the Machinery Vibration Severity Chart, with conditions plotted.

        - Duct Leakage Testing:

          - Witness the duct pressure testing performed by the mechanical/installing contractor.

          - Verify that proper test methods are used and that leakage rates are within specified tolerances.

          - Report any deficiencies observed.

        - Controls Verification

          - In conjunction with system balancing perform the following:

            - Work with the temperature control contractor to ensure the system is operating within the design limitations, and gain a mutual understanding of intended control performance.

            - Confirm that the sequences of operation are in compliance with the approved drawings.

            - Verify that controllers are calibrated and function as intended.

            - Verify that controller setpoints are as specified.

            - Verify the operation of lockout or interlock systems.

            - Verify the operation of all valve and damper actuators.

            - Verify that all controlled devices are properly installed and connected to the correct controller.

            - Verify that all controlled devices travel freely and are in the position indicated by the controller: open, closed, or modulating.

            - Verify the location and installation of all sensors to ensure they will sense only the intended temperatures, humidities, or pressures.

          - Reporting

            - The report shall include a summary of verifications performed, remaining deficiencies, and any variations from specified conditions.

END OF SECTION 230593